|  | . |
| --- | --- |

Technical specification to the purchasing procedure “2100158225 / 2200133401 GDL11 and GDL12 softened water pumps”.

Centrifugal pump complete with electric motor.
The pump is intended for pumping softened water. The electric motor is suitable for operation and power supply either via a frequency inverter (VFD) or directly from the mains power supply, in order to maintain the required pressure in the system.

Manufacturer: Leszczyńska Fabryka Pomp
Type: 150PJM215 DMa6

The pump impeller is mounted directly on the motor shaft. Horizontal axial suction and vertical upward discharge arrangement.

The supplied pump shall be equipped with a mechanical seal, type ANGA.
Flanged connections: DN200 / DN150, PN16.

Operating parameters:

- Pump capacity: approx. 220 m³/h

- Discharge pressure: 0.54 MPa

- Pumped medium temperature: 12–28°C

- Motor power: 55 kW

- Supply voltage: 400 V

Required documentation:

- Technical and operational documentation (DTR) for the pump and motor (wiring diagrams, drawings, manuals, etc.)

- Instructions for: transport, installation, maintenance, commissioning and shutdown

- List of causes of failures and troubleshooting methods

- Cross-sections and assembly drawings

- List of spare parts with catalogue numbers

- Documentation for the ANGA mechanical seal (connection diagrams, drawings, instructions, etc.)

- Electrical connection diagrams

- CE Declaration of Conformity

All documents supplied with the equipment shall be provided in Polish, in both hard copy and electronic form (PDF format compatible with Adobe Acrobat Reader, CD).

The supplied equipment shall comply with ORLEN S.A. Technical Standards for Rotating Machinery, including technical requirements for the manufacture and acceptance of pumps, as well as Electrical Industry Technical Requirements – WTBE 2.9. The above documents will be made available to Bidders during the site visit.

Warranty:
Minimum 24 months for both the pump and the motor.

A mandatory site visit is required prior to submitting an offer.